GEORGIA UNDERGROUND UTILITY 
MARKING STANDARDS

White Lining
The purpose of white lining the area to be located is to allow everyone involved with the dig site to know the exact location of the proposed excavation.  White-lining the excavation site is an excellent way to assist the locators in marking lines in your work area right the first time and in less time. This technique eliminates guessing by the locator about where the excavation will be done. In short, pre-marking the area and the extent of the intended excavation can reduce delays and the time it takes to conduct the locate.

White lining is a practice that has been widely used in the United States where the National Transportation Board concluded that pre-marking is a practice that helps prevent excavation damage. The procedure simply involves an excavator using white paint to indicate the route or area that is going to be excavated, such that the locator then knows exactly how much marking is required and where. White lining reduces confusion about what was marked or not marked. 
The UPC shall establish a policy and procedure which identify when white lining is required. (O.C.G.A. 25-9-4(a)(1)
Examples of areas to be white lined are smaller or linear excavations such as telecommunication drops, service lines such as water, gas and sewer, utility pits, cuts and repairs, curb repairs, bore holes, pole and signage placement, etc.  

White lining will not be required in the following situations:

1. Any large project so designated in accordance with GPSC Rule 515-9-4-.13 

    2.   Any jobsite that can be described with such particularity as required by O.C.G.A. 25-9-6(b)
White lining proposed dig sites that will follow a single path or trench shall be marked using white lines &/or arrows and located for twenty (20) feet on either side of the white line. It is important to identify the starting & ending points.


Facility Marking 
Facility owners shall indicate their facilities by placing their UPC alpha code, along with the type material that the facility consists of, at the beginning & end of locates. Also, arrows should be placed at the ends of markings to indicate that the underground facility continues.  In accomplishing the locate task, the line locator shall use all industry approved methods of locating including current maps of the utility system.
To avoid confusion on long runs, the marks shall be frequent enough to identify the owner.

The marks shall indicate the approximate center-line of the underground lines. For example, the middle of the cable, line or pipe shall be at the center of the dashed marks.

Location marks shall be 4 to 12 inches in length & at intervals of 5 to 10 feet.

[image: image1.png]5 ft. to 10 ft. intervals
N v

N
4inches to 12 inches




The line locator (person marking the lines) shall extend marks outside the proposed work area by 20 to 30 feet if those facilities extend outside the proposed excavation area. 

[image: image2.jpg]| I
(-MWA-E— - H— MWAD
0 0




In areas such as flower beds, rock gardens, etc., flags or stakes may be an alternative to paint. The decision to use flags, paint, or stakes shall be based on the terrain & job conditions. For instance, flags or stakes in wet areas, offsets in dirt construction zones that have a high volume of traffic crossing their line location marks.

[image: image11.png]




Dead ends, stub-outs, termination points, etc., shall be marked as follows:

[image: image3.jpg]



Lines that have lateral connections (T's) or changes in directions shall be clearly indicated. Marks indicating lateral connections shall clearly show the intersection & path of the lateral. Marks that show changes in direction shall be placed closer together for more accuracy.

[image: image4.jpg]Line Connectons, "['4
%

(—MWA—-—ﬁl—:\J—MWAé
CATT— — | —ATT—

MWA 1y e cross but do not connect



 
Manhole valves shall be identified by using a circle & letters if they are not visible (dirt covering valve boxes or pavement covering manhole cover).

[image: image5.png]



[image: image12.jpg]b ;4
bl

CMWA- —:- —MWAS
!
TT

A
p Y



Facilities that cross but do not intersect shall be marked as described to indicate such installation manner.
Unlocatable sewer laterals shall be marked by placing a green triangle on the sewer main at the tap pointing to the address served by the lateral.
[image: image6.jpg]MWAD




When facilities share the same trench, they shall be heavily identified & separated enough so that they can be readily identified. This would apply to lines that share the same color code. For example, cable television & telephone lines:

[image: image7.jpg]



If the facility to be marked has a diameter greater than 12”, the size of the facility shall be indicated if known.  If the size is not known, then the mark shall indicate greater that 12”.
Duct structures shall be marked by using a dot with parallel boundary on each side of the dot.
[image: image8.jpg]



In areas where there is a strong likelihood that any or all marker types showing line location would be destroyed, offsets shall be placed on a permanent surface. However, offsets should be used only in conjunction with marks placed above a facility. Offset spacing should be every third or fourth mark. For example, the following mark would indicate the line is 16 feet from the end of the arrow. 
[image: image9.jpg]



In areas where cables are spliced the facilities should be located individually as long as possible on both sides of the splice. When the signal is distorted due to the near proximity to the splice a circle with “SP” should indicate the area of distortion or “splice pit”. 
[image: image10.jpg]



